## Sheet1
Insulation Resistance Test & Continuity Test
.322" conductor wire: |  | NSF
NSF WIRE #: 17-C179
Test Date: |  | 2022-01-13
Ambient Air Temperature: |  | 41.9 | degrees F
Spool End Tape: |  |  | 9997 | meters
Outside Tape: |  |  | 164 | meters
Resistance per kilometer (conductors): |  |  | 0.0308 | ohms/meter
Theoretical conductor resistance: |  |  | 302.8564 | ohms
Model 1060 AEMC Megger
S/N:
Test from: | From termination, through drum, slipring, & connections down to Computer Lab
Insulation Resistance
Insulation resistance testing is made at 250V charge, applied
continuously for ten minutes. Results show in ohms, DAR, PI
and microfarads.
WIRES | Ohms (Gohms) | DAR | PI | uF
Red-White | 23.41 | 1.19 | 0.85 | 0.727
Red-Black | 9.21 | 1.18 | 0.79 | 0.765
Red-Green | 63.3 | 1.48 | 2.6 | 1.107
Black-White | 51.1 | 1 | 1.68 | 0.764
Black-Green | 58.2 | 1.58 | 3.54 | 1.092
White-Green | 56.6 | 1.42 | 2.13 | 1.17
Test from: | Computer Lab through connections up to O2 deck, slipring, drum, all the way to termination end
Insulation Resistance
Insulation resistance testing is made at 250V charge, applied
continuously for ten minutes. Results show in ohms, DAR, PI
and microfarads.
WIRES | Ohms (Gohms) | DAR | PI | uF
Red-White | 133.6 | 1.57 | 2.3 | 0.769
Red-Black | 122.5 | 1.97 | 1.94 | 0.727
Red-Green | 67.4 | 1.35 | 3.25 | 1.102
Black-White | 136.8 | 1.74 | 3.06 | 0.767
Black-Green | 57 | 1.27 | 2.48 | 1.099
White-Green | 76.1 | 1.56 | 2.59 | 1.168
Continuity Test
Continuity testing is made at the 400kohm setting,
applied for 60 seconds. Results are in Ohms.
WIRES | Resistance (Ohms)
Red-Green | 289 | Ohms
Black-Green | 290 | Ohms
White-Green | 291 | Ohms
Green-Ship | 0.5 | Ohms
Insulation Resistance Test & Continuity Test
.322" conductor wire: |  | NSF
NSF WIRE #: 17-C179
Test Date: |  | 2022-01-25
Ambient Air Temperature: |  | 39.6 | degrees F
Test from: | wire on drum only from termination end up through drum
Insulation Resistance
Insulation resistance testing is made at 250V charge, applied
continuously for ten minutes. Results show in ohms, DAR, PI
and microfarads.
WIRES | Ohms (Gohms) | DAR | PI | uF
Red-White | 163 | 1.55 | 2.52 | 0.721
Red-Black | 191.5 | 1.66 | 3.31 | 0.724
Red-Green | 129 | 1.7 | 3.68 | 1.098
Black-White | 233.6 | 1.8 | 3.03 | 0.719
Black-Green | 89.1 | 1.62 | 2.37 | 1.098
White-Green | 255.9 | 1.85 | 4.75 | 1.157
Continuity Test
Continuity testing is made at the 400kohm setting,
applied for 60 seconds. Results are in Ohms.
continuity measured at termination end
WIRES | Resistance (Ohms) Fluke |  | Resistance (Ohms)
Red-Green | 271.2 | Ohms | 268.5 | Ohms
Black-Green | 271.6 | Ohms | 269 | Ohms
White-Green | 268 | Ohms | 271 | Ohms
Red-White | 535 | Ohms | 544 | Ohms
White-Black | 541 | Ohms | 536 | Ohms
Black-Red | 541 | Ohms | 536 | Ohms
Green-Ship | 0.51 | Ohms | 0.8 | Ohms
Test Date: |  | 2022-01-26
Ambient Air Temperature: |  | 24 | degrees F
Test from: | wire on drum only: from drum end down through termination
Insulation Resistance
Insulation resistance testing is made at 250V charge, applied
continuously for ten minutes. Results show in ohms, DAR, PI
and microfarads.
WIRES | Ohms (Gohms) | DAR | PI | uF
Red-White | 489 | 1.77 | 5.29 | 0.764
Red-Black | 515 | 1.59 | 6.77 | 0.762
Red-Green | 397 | 1.89 | 7.61 | 1.171
Black-White | 499 | 1.8 | 5.02 | 0.76
Black-Green | 328.6 | 1.92 | 5.36 | 1.091
White-Green | 963 | 1.67 | 12.32 | 1.101